## Sheet1
Name | Description | Signal Type | Signal Location
R010_FCV_122_wOutCommand | Flow control valve - Cooling water flow through purification system | AO_4-20mA | Main Cabinet
R010_FIT_122_wInValue | Cooling water flow through water purification system R010 | AI_4-20mA | Main Cabinet
R010_PDS_151_bInInput | Differential pressure switch for police filter R010-F-101 | DI_24VDC | Main Cabinet
R010_PDT_152_wInValue | Differential pressure - pressure drop over ion exchangers | AI_4-20mA | Main Cabinet
R010_PSA_001_bInInput | Instrument air supply pressure in instrument air cabinet | DI_24VDC | Main Cabinet
R010_QT_150_wInValue | Conductivity transmitter for conductivity measurement of outgoing purified cooling water | AI_4-20mA | Main Cabinet
R010_TT_153_wInValue | Unpurified cooling water inlet temperature to purification system | AI_4-20mA | Main Cabinet
R010_YSV_101_bInSignalHome | Unpurified cooling water inlet on-off valve to ion exchanger vessel R010-F-100 | DI_24VDC | Main Cabinet
R010_YSV_101_bInSignalWork | Unpurified cooling water inlet on-off valve to ion exchanger vessel R010-F-100 | DI_24VDC | Main Cabinet
R010_YSV_101_bOutCommandHome | Unpurified cooling water inlet on-off valve to ion exchanger vessel R010-F-100 | DO_24VDC | Main Cabinet
R010_YSV_101_bOutCommandWork | Unpurified cooling water inlet on-off valve to ion exchanger vessel R010-F-100 | DO_24VDC | Main Cabinet
R010_YSV_104_bInSignalHome | Resin fill on-off valve to ion exchanger vessel R010-F-100 | DI_24VDC | Main Cabinet
R010_YSV_104_bInSignalWork | Resin fill on-off valve to ion exchanger vessel R010-F-100 | DI_24VDC | Main Cabinet
R010_YSV_104_bOutCommandHome | Resin fill on-off valve to ion exchanger vessel R010-F-100 | DO_24VDC | Main Cabinet
R010_YSV_104_bOutCommandWork | Resin fill on-off valve to ion exchanger vessel R010-F-100 | DO_24VDC | Main Cabinet
R010_YSV_105_bInSignalHome | Purified cooling water outlet on-off valve from ion exchanger vessel R010-F-100 | DI_24VDC | Main Cabinet
R010_YSV_105_bInSignalWork | Purified cooling water outlet on-off valve from ion exchanger vessel R010-F-100 | DI_24VDC | Main Cabinet
R010_YSV_105_bOutCommandHome | Purified cooling water outlet on-off valve from ion exchanger vessel R010-F-100 | DO_24VDC | Main Cabinet
R010_YSV_105_bOutCommandWork | Purified cooling water outlet on-off valve from ion exchanger vessel R010-F-100 | DO_24VDC | Main Cabinet
R010_YSV_106_bInSignalHome | Deionized water inlet on-off valve to ion exchanger vessel R010-F-100 | DI_24VDC | Main Cabinet
R010_YSV_106_bInSignalWork | Deionized water inlet on-off valve to ion exchanger vessel R010-F-100 | DI_24VDC | Main Cabinet
R010_YSV_106_bOutCommandHome | Deionized water inlet on-off valve to ion exchanger vessel R010-F-100 | DO_24VDC | Main Cabinet
R010_YSV_106_bOutCommandWork | Deionized water inlet on-off valve to ion exchanger vessel R010-F-100 | DO_24VDC | Main Cabinet
R010_YSV_107_bInSignalHome | Resin drain on-off valve from ion exchanger vessel R010-F-100 | DI_24VDC | Main Cabinet
R010_YSV_107_bInSignalWork | Resin drain on-off valve from ion exchanger vessel R010-F-100 | DI_24VDC | Main Cabinet
R010_YSV_107_bOutCommandHome | Resin drain on-off valve from ion exchanger vessel R010-F-100 | DO_24VDC | Main Cabinet
R010_YSV_107_bOutCommandWork | Resin drain on-off valve from ion exchanger vessel R010-F-100 | DO_24VDC | Main Cabinet
R010_YSV_109_bInSignalHome | Off-gas extraction connection on-off valve from ion exchanger vessel R010-F-100 | DI_24VDC | Main Cabinet
R010_YSV_109_bInSignalWork | Off-gas extraction connection on-off valve from ion exchanger vessel R010-F-100 | DI_24VDC | Main Cabinet
R010_YSV_109_bOutCommandHome | Off-gas extraction connection on-off valve from ion exchanger vessel R010-F-100 | DO_24VDC | Main Cabinet
R010_YSV_109_bOutCommandWork | Off-gas extraction connection on-off valve from ion exchanger vessel R010-F-100 | DO_24VDC | Main Cabinet
R010_YSV_111_bInSignalHome | Unpurified cooling water inlet on-off valve to ion exchanger vessel R010-F-110 | DI_24VDC | Main Cabinet
R010_YSV_111_bInSignalWork | Unpurified cooling water inlet on-off valve to ion exchanger vessel R010-F-110 | DI_24VDC | Main Cabinet
R010_YSV_111_bOutCommandHome | Unpurified cooling water inlet on-off valve to ion exchanger vessel R010-F-110 | DO_24VDC | Main Cabinet
R010_YSV_111_bOutCommandWork | Unpurified cooling water inlet on-off valve to ion exchanger vessel R010-F-110 | DO_24VDC | Main Cabinet
R010_YSV_114_bInSignalHome | Resin fill on-off valve to ion exchanger vessel R010-F-110 | DI_24VDC | Main Cabinet
R010_YSV_114_bInSignalWork | Resin fill on-off valve to ion exchanger vessel R010-F-110 | DI_24VDC | Main Cabinet
R010_YSV_114_bOutCommandHome | Resin fill on-off valve to ion exchanger vessel R010-F-110 | DO_24VDC | Main Cabinet
R010_YSV_114_bOutCommandWork | Resin fill on-off valve to ion exchanger vessel R010-F-110 | DO_24VDC | Main Cabinet
R010_YSV_115_bInSignalHome | Purified cooling water outlet on-off valve from ion exchanger vessel R010-F-110 | DI_24VDC | Main Cabinet
R010_YSV_115_bInSignalWork | Purified cooling water outlet on-off valve from ion exchanger vessel R010-F-110 | DI_24VDC | Main Cabinet
R010_YSV_115_bOutCommandHome | Purified cooling water outlet on-off valve from ion exchanger vessel R010-F-110 | DO_24VDC | Main Cabinet
R010_YSV_115_bOutCommandWork | Purified cooling water outlet on-off valve from ion exchanger vessel R010-F-110 | DO_24VDC | Main Cabinet
R010_YSV_116_bInSignalHome | Deionized water inlet on-off valve to ion exchanger vessel R010-F-110 | DI_24VDC | Main Cabinet
R010_YSV_116_bInSignalWork | Deionized water inlet on-off valve to ion exchanger vessel R010-F-110 | DI_24VDC | Main Cabinet
R010_YSV_116_bOutCommandHome | Deionized water inlet on-off valve to ion exchanger vessel R010-F-110 | DO_24VDC | Main Cabinet
R010_YSV_116_bOutCommandWork | Deionized water inlet on-off valve to ion exchanger vessel R010-F-110 | DO_24VDC | Main Cabinet
R010_YSV_117_bInSignalHome | Resin drain on-off valve from ion exchanger vessel R010-F-110 | DI_24VDC | Main Cabinet
R010_YSV_117_bInSignalWork | Resin drain on-off valve from ion exchanger vessel R010-F-110 | DI_24VDC | Main Cabinet
R010_YSV_117_bOutCommandHome | Resin drain on-off valve from ion exchanger vessel R010-F-110 | DO_24VDC | Main Cabinet
R010_YSV_117_bOutCommandWork | Resin drain on-off valve from ion exchanger vessel R010-F-110 | DO_24VDC | Main Cabinet
R010_YSV_119_bInSignalHome | Off-gas extraction connection on-off valve from ion exchanger vessel R010-F-110 | DI_24VDC | Main Cabinet
R010_YSV_119_bInSignalWork | Off-gas extraction connection on-off valve from ion exchanger vessel R010-F-110 | DI_24VDC | Main Cabinet
R010_YSV_119_bOutCommandHome | Off-gas extraction connection on-off valve from ion exchanger vessel R010-F-110 | DO_24VDC | Main Cabinet
R010_YSV_119_bOutCommandWork | Off-gas extraction connection on-off valve from ion exchanger vessel R010-F-110 | DO_24VDC | Main Cabinet
R011_FCV_222_wOutCommand | Flow control valve - Cooling water flow through purification system | AO_4-20mA | Main Cabinet
R011_FIT_222_wInValue | Cooling water flow through water purification system R011 | AI_4-20mA | Main Cabinet
R011_FIT_254_wInValue | Cleaning water flow and volume when cleaning the ion exchange vessels | AI_4-20mA | Main Cabinet
R011_PDS_251_bInInput | Differential pressure switch for police filter R011-F-201 | DI_24VDC | Main Cabinet
R011_PDT_252_wInValue | Differential pressure - pressure drop over ion exchangers | AI_4-20mA | Main Cabinet
R011_PSA_001_bInInput | Instrument air supply pressure in instrument air cabinet | DI_24VDC | Main Cabinet
R011_QT_250_wInValue | Conductivity transmitter for conductivity measurement of outgoing purified cooling water | AI_4-20mA | Main Cabinet
R011_TT_253_wInValue | Unpurified cooling water inlet temperature to purification system | AI_4-20mA | Main Cabinet
R011_YSV_201_bInSignalHome | Unpurified cooling water inlet on-off valve to ion exchanger vessel R011-F-200 | DI_24VDC | Main Cabinet
R011_YSV_201_bInSignalWork | Unpurified cooling water inlet on-off valve to ion exchanger vessel R011-F-200 | DI_24VDC | Main Cabinet
R011_YSV_201_bOutCommandHome | Unpurified cooling water inlet on-off valve to ion exchanger vessel R011-F-200 | DO_24VDC | Main Cabinet
R011_YSV_201_bOutCommandWork | Unpurified cooling water inlet on-off valve to ion exchanger vessel R011-F-200 | DO_24VDC | Main Cabinet
R011_YSV_204_bInSignalHome | Resin fill on-off valve to ion exchanger vessel R011-F-200 | DI_24VDC | Main Cabinet
R011_YSV_204_bInSignalWork | Resin fill on-off valve to ion exchanger vessel R011-F-200 | DI_24VDC | Main Cabinet
R011_YSV_204_bOutCommandHome | Resin fill on-off valve to ion exchanger vessel R011-F-200 | DO_24VDC | Main Cabinet
R011_YSV_204_bOutCommandWork | Resin fill on-off valve to ion exchanger vessel R011-F-200 | DO_24VDC | Main Cabinet
R011_YSV_205_bInSignalHome | Purified cooling water outlet on-off valve from ion exchanger vessel R011-F-200 | DI_24VDC | Main Cabinet
R011_YSV_205_bInSignalWork | Purified cooling water outlet on-off valve from ion exchanger vessel R011-F-200 | DI_24VDC | Main Cabinet
R011_YSV_205_bOutCommandHome | Purified cooling water outlet on-off valve from ion exchanger vessel R011-F-200 | DO_24VDC | Main Cabinet
R011_YSV_205_bOutCommandWork | Purified cooling water outlet on-off valve from ion exchanger vessel R011-F-200 | DO_24VDC | Main Cabinet
R011_YSV_206_bInSignalHome | Deionized water inlet on-off valve to ion exchanger vessel R011-F-200 | DI_24VDC | Main Cabinet
R011_YSV_206_bInSignalWork | Deionized water inlet on-off valve to ion exchanger vessel R011-F-200 | DI_24VDC | Main Cabinet
R011_YSV_206_bOutCommandHome | Deionized water inlet on-off valve to ion exchanger vessel R011-F-200 | DO_24VDC | Main Cabinet
R011_YSV_206_bOutCommandWork | Deionized water inlet on-off valve to ion exchanger vessel R011-F-200 | DO_24VDC | Main Cabinet
R011_YSV_207_bInSignalHome | Resin drain on-off valve from ion exchanger vessel R011-F-200 | DI_24VDC | Main Cabinet
R011_YSV_207_bInSignalWork | Resin drain on-off valve from ion exchanger vessel R011-F-200 | DI_24VDC | Main Cabinet
R011_YSV_207_bOutCommandHome | Resin drain on-off valve from ion exchanger vessel R011-F-200 | DO_24VDC | Main Cabinet
R011_YSV_207_bOutCommandWork | Resin drain on-off valve from ion exchanger vessel R011-F-200 | DO_24VDC | Main Cabinet
R011_YSV_209_bInSignalHome | Off-gas extraction connection on-off valve from ion exchanger vessel R011-F-200 | DI_24VDC | Main Cabinet
R011_YSV_209_bInSignalWork | Off-gas extraction connection on-off valve from ion exchanger vessel R011-F-200 | DI_24VDC | Main Cabinet
R011_YSV_209_bOutCommandHome | Off-gas extraction connection on-off valve from ion exchanger vessel R011-F-200 | DO_24VDC | Main Cabinet
R011_YSV_209_bOutCommandWork | Off-gas extraction connection on-off valve from ion exchanger vessel R011-F-200 | DO_24VDC | Main Cabinet
R011_YSV_211_bInSignalHome | Unpurified cooling water inlet on-off valve to ion exchanger vessel R011-F-210 | DI_24VDC | Main Cabinet
R011_YSV_211_bInSignalWork | Unpurified cooling water inlet on-off valve to ion exchanger vessel R011-F-210 | DI_24VDC | Main Cabinet
R011_YSV_211_bOutCommandHome | Unpurified cooling water inlet on-off valve to ion exchanger vessel R011-F-210 | DO_24VDC | Main Cabinet
R011_YSV_211_bOutCommandWork | Unpurified cooling water inlet on-off valve to ion exchanger vessel R011-F-210 | DO_24VDC | Main Cabinet
R011_YSV_214_bInSignalHome | Resin fill on-off valve to ion exchanger vessel R011-F-210 | DI_24VDC | Main Cabinet
R011_YSV_214_bInSignalWork | Resin fill on-off valve to ion exchanger vessel R011-F-210 | DI_24VDC | Main Cabinet
R011_YSV_214_bOutCommandHome | Resin fill on-off valve to ion exchanger vessel R011-F-210 | DO_24VDC | Main Cabinet
R011_YSV_214_bOutCommandWork | Resin fill on-off valve to ion exchanger vessel R011-F-210 | DO_24VDC | Main Cabinet
R011_YSV_215_bInSignalHome | Purified cooling water outlet on-off valve from ion exchanger vessel R011-F-210 | DI_24VDC | Main Cabinet
R011_YSV_215_bInSignalWork | Purified cooling water outlet on-off valve from ion exchanger vessel R011-F-210 | DI_24VDC | Main Cabinet
R011_YSV_215_bOutCommandHome | Purified cooling water outlet on-off valve from ion exchanger vessel R011-F-210 | DO_24VDC | Main Cabinet
R011_YSV_215_bOutCommandWork | Purified cooling water outlet on-off valve from ion exchanger vessel R011-F-210 | DO_24VDC | Main Cabinet
R011_YSV_216_bInSignalHome | Deionized water inlet on-off valve to ion exchanger vessel R011-F-210 | DI_24VDC | Main Cabinet
R011_YSV_216_bInSignalWork | Deionized water inlet on-off valve to ion exchanger vessel R011-F-210 | DI_24VDC | Main Cabinet
R011_YSV_216_bOutCommandHome | Deionized water inlet on-off valve to ion exchanger vessel R011-F-210 | DO_24VDC | Main Cabinet
R011_YSV_216_bOutCommandWork | Deionized water inlet on-off valve to ion exchanger vessel R011-F-210 | DO_24VDC | Main Cabinet
R011_YSV_217_bInSignalHome | Resin drain on-off valve from ion exchanger vessel R011-F-210 | DI_24VDC | Main Cabinet
R011_YSV_217_bInSignalWork | Resin drain on-off valve from ion exchanger vessel R011-F-210 | DI_24VDC | Main Cabinet
R011_YSV_217_bOutCommandHome | Resin drain on-off valve from ion exchanger vessel R011-F-210 | DO_24VDC | Main Cabinet
R011_YSV_217_bOutCommandWork | Resin drain on-off valve from ion exchanger vessel R011-F-210 | DO_24VDC | Main Cabinet
R011_YSV_219_bInSignalHome | Off-gas extraction connection on-off valve from ion exchanger vessel R011-F-210 | DI_24VDC | Main Cabinet
R011_YSV_219_bInSignalWork | Off-gas extraction connection on-off valve from ion exchanger vessel R011-F-210 | DI_24VDC | Main Cabinet
R011_YSV_219_bOutCommandHome | Off-gas extraction connection on-off valve from ion exchanger vessel R011-F-210 | DO_24VDC | Main Cabinet
R011_YSV_219_bOutCommandWork | Off-gas extraction connection on-off valve from ion exchanger vessel R011-F-210 | DO_24VDC | Main Cabinet
R011_YSV_224_bInSignalHome | Resin flush on-off valve | DI_24VDC | Main Cabinet
R011_YSV_224_bInSignalWork | Resin flush on-off valve | DI_24VDC | Main Cabinet
R011_YSV_224_bOutCommandHome | Resin flush on-off valve | DO_24VDC | Main Cabinet
R011_YSV_224_bOutCommandWork | Resin flush on-off valve | DO_24VDC | Main Cabinet
R001_FIT_113_wInValue | Flow transmitter for measuring primary cooling water flow in main loop | AI_4-20mA | Remote Cabinet
R001_PIT_114_wInValue | Pressure transmitter for cooling water pressure upstream cooled objects | AI_4-20mA | Remote Cabinet
R001_PIT_118_wInValue | Pressure transmitter measuring pressure after cooled objects | AI_4-20mA | Remote Cabinet
R001_PSA_001_bInInput | Instrument air supply pressure in instrument air cabinet | DI_24VDC | Remote Cabinet
R001_PSZ_101_bInInput | Pressure switch for over-pressure protection of lower reactor | DI_24VDC | Remote Cabinet
R001_PSZ_102_bInInput | Pressure switch for over-pressure protection of lower reactor | DI_24VDC | Remote Cabinet
R001_PSZ_103_bInInput | Pressure switch for over-pressure protection of upper reactor | DI_24VDC | Remote Cabinet
R001_PSZ_104_bInInput | Pressure switch for over-pressure protection of upper reactor | DI_24VDC | Remote Cabinet
R001_QIT_112_wInValue | Conductivity transmitter for conductivity measurement in main cooling loop | AI_4-20mA | Remote Cabinet
R001_SICA_001_bInSignalContactor | Frequency converter controlling pump R001-P-001 | DI_24VDC | Remote Cabinet
R001_SICA_001_wInSpeedAct | Frequency converter controlling pump R001-P-001 | AI_4-20mA | Remote Cabinet
R001_SICA_001_bInMotorProtector | Frequency converter controlling pump R001-P-001 | DI_24VDC | Remote Cabinet
R001_SICA_001_bInLocalDisconnect | Frequency converter controlling pump R001-P-001 | DI_24VDC | Remote Cabinet
R001_SICA_001_wOutSpeedSetpoint | Frequency converter controlling pump R001-P-001 | AO_4-20mA | Remote Cabinet
R001_SICA_001_bOutContactor | Frequency converter controlling pump R001-P-001 | DO_24VDC | Remote Cabinet
R001_SICA_002_bInSignalContactor | Frequency converter controlling pump R001-P-002 | DI_24VDC | Remote Cabinet
R001_SICA_002_wInSpeedAct | Frequency converter controlling pump R001-P-002 | AI_4-20mA | Remote Cabinet
R001_SICA_002_bInMotorProtector | Frequency converter controlling pump R001-P-002 | DI_24VDC | Remote Cabinet
R001_SICA_002_bInLocalDisconnect | Frequency converter controlling pump R001-P-002 | DI_24VDC | Remote Cabinet
R001_SICA_002_wOutSpeedSetpoint | Frequency converter controlling pump R001-P-002 | AO_4-20mA | Remote Cabinet
R001_SICA_002_bOutContactor | Frequency converter controlling pump R001-P-002 | DO_24VDC | Remote Cabinet
R001_TT_109_wInValue | Primary cooling water temperature downstream R001-W-001 | AI_4-20mA | Remote Cabinet
R002_FIT_113_wInValue | Flow transmitter for measuring primary cooling water flow in main loop | AI_4-20mA | Machine 1
R002_PIT_114_wInValue | Pressure transmitter for cooling water pressure upstream cooled objects | AI_4-20mA | Machine 1
R002_PIT_118_wInValue | Pressure transmitter measuring pressure after cooled objects | AI_4-20mA | Machine 1
R002_PSA_001_bInInput | Instrument air supply pressure in instrument air cabinet | DI_24VDC | Machine 1
R002_PSZ_101_bInInput | Pressure switch for over-pressure protection of upper reactor | DI_24VDC | Machine 1
R002_PSZ_102_bInInput | Pressure switch for over-pressure protection of lower reactor | DI_24VDC | Machine 1
R002_QIT_112_wInValue | Conductivity transmitter for conductivity measurement in main cooling loop | AI_4-20mA | Machine 1
R002_SICA_005_bInSignalContactor | Frequency converter controlling pump R002-P-005 | DI_24VDC | Machine 1
R002_SICA_005_wInSpeedAct | Frequency converter controlling pump R002-P-005 | AI_4-20mA | Machine 1
R002_SICA_005_bInMotorProtector | Frequency converter controlling pump R002-P-005 | DI_24VDC | Machine 1
R002_SICA_005_bInLocalDisconnect | Frequency converter controlling pump R002-P-005 | DI_24VDC | Machine 1
R002_SICA_005_wOutSpeedSetpoint | Frequency converter controlling pump R002-P-005 | AO_4-20mA | Machine 1
R002_SICA_005_bOutContactor | Frequency converter controlling pump R002-P-005 | DO_24VDC | Machine 1
R002_SICA_006_bInSignalContactor | Frequency converter controlling pump R002-P-006 | DI_24VDC | Machine 1
R002_SICA_006_wInSpeedAct | Frequency converter controlling pump R002-P-006 | AI_4-20mA | Machine 1
R002_SICA_006_bInMotorProtector | Frequency converter controlling pump R002-P-006 | DI_24VDC | Machine 1
R002_SICA_006_bInLocalDisconnect | Frequency converter controlling pump R002-P-006 | DI_24VDC | Machine 1
R002_SICA_006_wOutSpeedSetpoint | Frequency converter controlling pump R002-P-006 | AO_4-20mA | Machine 1
R002_SICA_006_bOutContactor | Frequency converter controlling pump R002-P-006 | DO_24VDC | Machine 1
R002_TT_109_wInValue | Primary cooling water temperature downstream R002-W-003 | AI_4-20mA | Machine 1
R004_FCV_110_wOutCommand | Flow control valve for minimum cooling water flow - by-pass valve | AO_4-20mA | Machine 1
R004_PDT_106_wInValue | Differential pressure transmitter for measuring intermediate cooling water flow to reactors primary cooling | AI_4-20mA | Machine 1
R004_PDT_107_wInValue | Differential pressure transmitter for measuring intermediate cooling water flow to convertors primary cooling | AI_4-20mA | Machine 1
R004_PDT_110_wInValue | Differential pressure transmitter for measuring intermediate cooling water flow | AI_4-20mA | Machine 1
R004_PDT_115_wInValue | Differential pressure transmitter for measuring ext. supply cooling water flow | AI_4-20mA | Machine 1
R004_PDT_120_wInValue | Differential pressure transmitter for measuring intermediate cooling water flow to nitrogen gas treatment | AI_4-20mA | Machine 1
R004_PSA_001_bInInput | Instrument air supply pressure in instrument air cabinet | DI_24VDC | Machine 1
R004_PT_104_wInValue | Pressure transmitter measuring supply pressure to cooled objects | AI_4-20mA | Machine 1
R004_SICA_104_bInSignalContactor | Frequency converter controlling pump R004-P-007 | DI_24VDC | Machine 1
R004_SICA_104_wInSpeedAct | Frequency converter controlling pump R004-P-007 | AI_4-20mA | Machine 1
R004_SICA_104_bInMotorProtector | Frequency converter controlling pump R004-P-007 | DI_24VDC | Machine 1
R004_SICA_104_bInLocalDisconnect | Frequency converter controlling pump R004-P-007 | DI_24VDC | Machine 1
R004_SICA_104_wOutSpeedSetpoint | Frequency converter controlling pump R004-P-007 | AO_4-20mA | Machine 1
R004_SICA_104_bOutContactor | Frequency converter controlling pump R004-P-007 | DO_24VDC | Machine 1
R004_TCV_107_wOutCommand | Temperature control valve - ext. supply cooling water | AO_4-20mA | Machine 1
R004_TCV_118_wOutCommand | Temperature control valve - convertors cooling water | AO_4-20mA | Machine 1
R004_TCV_119_wOutCommand | Temperature control valve - reactors cooling water | AO_4-20mA | Machine 1
R004_TT_103_wInValue | Intermediate cooling water temperature upstream R004-W-005 | AI_4-20mA | Machine 1
R004_TT_105_wInValue | Ext. supply cooling water inlet temperature to heat exchanger R004-W-005 | AI_4-20mA | Machine 1
R004_TT_106_wInValue | Ext. supply cooling water outlet temperature from R004-W-005 | AI_4-20mA | Machine 1
R004_TT_107_wInValue | Intermediate cooling water temperature downstream R004-W-005 | AI_4-20mA | Machine 1
R004_TT_108_wInValue | Intermediate cooling water return temperature - reactors primary cooling | AI_4-20mA | Machine 1
R004_TT_110_wInValue | Intermediate cooling water return temperature - convertors primary cooling | AI_4-20mA | Machine 1
R004_TT_121_wInValue | Intermediate cooling water return temperature - nitrogen gas treatment | AI_4-20mA | Machine 1